## Sheet1
How to Use this Spreadsheet
Power: Each AKT-ECT-000-000 Bus coupler can provide 1750 mAmp of 5V logic power and 10 Amps of of 24V power for output power. If either of these current limits are exceeded by the total number of slice I/O modules a Power Feed Module can be added for an additional 1750 mAmp of logic power and 10 Amps of 24V output power. To use the tool enter the number of each available I/O slice in column C that will be on one Bus Coupler, and look at the totals in cells F34 and G34. If they exceed either max current limit (signified by the total displayed in red) an additional power feed module is required.
Data: Each AKT-ECT-000-000 Coupler can process up to 1024 Bytes
|  |  | DO NOT CHANGE | DO NOT CHANGE
Part Number | Description | Number of Slices | Internal bus current draw (per single slice) | 24 V Current Draw (per single slice) | Total Internal bus current draw | Total 24 V Current Draw | Total Input Data | Total Output Data | Input Data (per single slice) | Output Data (per single slice)
Input Modules
AKT-DN-004-000 | 4 Channel Digital Input Module, 3ms | 1 | 3 | 0 | 3 | 0 | 0.5 | 0 | 0.5 | 0
AKT-DNH-004-000 | 4 Channel Digital Input Module, .2ms | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0
AKT-DN-008-000 | 8 Channel Digital Input Module, 3ms | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 1 | 0
AKT-DNH-008-000 | 8 Channel Digital Input Module, .2ms | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 1 | 0
Output Modules
AKT-DT-004-000 | 4 Channel Digital Output Module, 0.5A | 6 | 39 | 2 | 234 | 12 | 0 | 3 | 0 | 0.5
AKT-DT-008-000 | 8 Channel Digital Output Module, 0.5A |  | 78 | 4 | 0 | 0 | 0 | 0 | 0 | 1
AKT-DT-2RT-000 | 2 Channel Relay Output Module, 2.0A, N/O |  | 85 | 0 | 0 | 0 | 0 | 0 | 0 | 0.25
Analog Input Modules
AKT-AN-410-000 | 4 Channel Analog Input Module, 0-10 Vdc | 2 | 100 | 0 | 200 | 0 | 24 | 24 | 12 | 12
AKT-AN-420-000 | 4 Channel Analog Input Module, 0-20 ma |  | 85 | 0 | 0 | 0 | 0 | 0 | 12 | 12
AKT-AN-810-000 | 8 Channel Analog Input Module, 0-10 Vdc |  | 140 | 0 | 0 | 0 | 0 | 0 | 24 | 24
AKT-AN-820-000 | 8 Channel Analog Input Module, 0-20 ma |  | 105 | 0 | 0 | 0 | 0 | 0 | 24 | 24
AKT-AN-200-000 | 2 Channel Thermocouple Input Module |  | 65 | 0 | 0 | 0 | 0 | 0 | 6 | 6
AKT-AN-400-000 | 4 Channel Thermocouple Input Module |  | 75 | 0 | 0 | 0 | 0 | 0 | 12 | 12
Analog Output Modules
AKT-AT-220-000 | 2 Channel Analog Output Module, 0-20 ma |  | 60 | 0.09 | 0 | 0 | 0 | 0 | 6 | 6
AKT-AT-410-000 | 4 Channel Analog Output Module, 0-10 Vdc |  | 20 | 0.008 | 0 | 0 | 0 | 0 | 12 | 12
AKT-AT-420-000 | 4 Channel Analog Output Module, 0-20 ma |  | 20 | 0.14 | 0 | 0 | 0 | 0 | 12 | 12
AKT-AT-810-000 | 8 Channel Analog Output Module, 0-10 Vdc |  | 20 | 0.016 | 0 | 0 | 0 | 0 | 24 | 24
AKT-AT-820-000 | 8 Channel Analog Output Module, 0-20 ma |  | 20 | 0.22 | 0 | 0 | 0 | 0 | 24 | 24
Specialty Modules
AKT-EM-000-000 | End Module |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
AKT-IM-000-000 | Isolation Module |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
AKT-PS-024-000 | Power Feed Module, 24 Vdc |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
AKT-PSF-024-000 | Power Feed Module, 24 Vdc, Fused |  | 0 | 0 | 0 | 0 | 0 | 0 | 0.25 | 0
|  |  |  | System Total | 437 | 12 | 24.5 | 27
|  |  |  | Max per Coupler | 1750 mAmps | 10 Amps | 1024 Bytes | 1024 Bytes
If additional 24 VDC power is needed:
Option 1: Use some of the slices with a separate ECT coupler in another bus terminal block
Option 2: The following 24 VDC power feed modules are available to insert in the row of slices to provide 24 volt power to all slices to the right
- AKT-PS-024-000
- AKT-PSF-024-000