## Sheet1
AKT2G Coupler Sizing
How to Use this Spreadsheet
Power: Each AKT2G-ECT-000-000 Bus coupler can provide 2 Amps (2000 mAmp) of 5V logic power and 10 Amps (10,000 mAmp) of 24V power for output power. If either of these current limits are exceeded by the total number of slice I/O modules a Power Feed Module can be added for an additional 10 Amps of 24V output power. To use the tool enter the number of each available I/O slice in column C that will be on one Bus Coupler, and look at the totals in cells F35 and G35. If they exceed either max current limit (signified by the total displayed in red) an additional power feed module is required.
Data: Each AKT2G-ECT-000-000 Coupler can process up to 1024 input and 1024 output bytes
Slice Quantity - The max number of slices connected to the coupler is 64
Part Number | Description | Number of Slices | Internal bus current draw (per single slice) | 24 V Current Draw (per single slice) mAmps | Total Internal bus current draw mAmps | Total 24 V Current Draw mAmps | Total Input Data bytes | Total Output Data bytes | Input Data (per single slice) | Output Data (per single slice) | Notes
Input Modules
AKT2G-DN-008-000 | 8-channel digital input terminal 24 V DC, filter 3.0 ms | 2 | 90 | 2 | 180 | 4 | 2 | 0 | 1 | 0
AKT2G-DNH-008-000 | 8-channel digital input terminal 24 V DC, filter 10 µs | 0 | 90 | 2 | 0 | 0 | 0 | 0 | 1 | 0 | typ. 2 mA + load
Output Modules
AKT2G-DT-008-000 | 8-channel digital output terminal 24 V DC, 0.5 A | 1 | 110 | 4000 | 110 | 4000 | 0 | 1 | 0 | 1
Analog Input Modules
AKT2G-AN-430-000 | 4-channel analog input, parameterisable, -10/0…+10 V, -20/0/+4…+20 mA, 16 bit |  | 170 | 2 | 340 | 0 | 0 | 0 | 8 | 0
AKT2G-AN-400-000 | 4-channel thermocouple input terminal, wire breakage detection, 16 bit | 1 | 140 | 2 | 280 | 2 | 8 | 0 | 8 | 0 | 4 x 16-bit AO output
Analog Output Modules
AKT2G-AT-410-000 | 4-channel analog output terminal 0…10 V, 12 bi |  | 140 | 25 | 0 | 0 | 0 | 0 | 0 | 8 | 4 x 16-bit AO output
AKT2G-AT-425-000 | 4-channel analog output terminal -10 V…+10 V, 12 bit | 1 | 140 | 25 | 140 | 25 | 0 | 8 | 0 | 8 | 4 x 16-bit AO output
Safety IO
AKT2G-SDI-004-000 | 4-channel digital input terminal, Safety, 24 V DC | 1 | 200 | 2 | 200 | 2 | 6 | 6 | 6 | 6
AKT2G-SDO-004-000 | 4-channel digital output terminal, Safety, 24 V DC, 0.5 A |  | 221 | 2000 | 0 | 0 | 0 | 0 | 6 | 6
Specialty Modules
AKT2G-DN-002-000 | Up/down counter 24 V DC, 100 kHz, 32 bit counter depth | 2 | 130 | 300 | 260 | 600 | 8 | 0 | 4 | 0 | typ. 14 mA + load
AKT2G-AN-240-000 | 2-channel input terminal PT100 (RTD) for resistance sensors, 16 bit |  | 190 | 1 | 0 | 0 | 0 | 0 | 8 | 0
AKT2G-ENC-180-000 | 1-channel incremental encoder interface, 32 bit | 0 | 130 | 300 | 0 | 0 | 0 | 0 | 6 | 5 |  | 0.1 A (excluding sensor load current) | 1 x 32/16-bit binary, switchable | 2000 of 300 is encoder current load
AKT2G-ENC-190-000 | Incremental encoder interface with differential input, 16/32 bit |  | 130 | 300 | 0 | 0 | 0 | 0 | 6 | 5 |  | 2000 of 300 is encoder current load | up to 6 bytes outputs, 22 bytes inputs, depends on parameterization
AKT2G-EM-000-000 | End Module | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
AKT2G-PSF-024-000 | Power supply terminal with fuse, 24 V DC (adds in 10 amps per slice) |  | 0 | 10000 | 0 | 0 | 0 | 0 | 0 | 0
* each power feed module supplies ann additional 10 amps of current |  |  |  | System Total: | 1510 | 4633 | 24 | 15
|  |  |  | Max per Coupler + added PSF slices: | 2000 | 10000 | 1024 | 1024
If additional 24 VDC power is needed:
Option 1: Use some of the slices with a separate AKT2G-ECT coupler in another bus terminal block
Option 2: The following 24 VDC power feed modules are available to insert in the row of slices (I/O lbock) to provide 24 volt power to all slices to the right:
- AKT2G-PSF-024-000
Note: : The Digital Output modules are rated for 0.5 amps per channel. In actuallity most Dig Output points will only need a faction of this amount
and in many appplications all outputs will not be turned on at the same time. Therefor the actual 24 VDC Digital Output current will be less than caluclated in ths spreadsheet. This could mean that
additional ECT couplers will not be needed
Cells with light green colored cells reflect the worse case loading number |  | Example: | 300
Cells with lightred colored cells mean the mximun r has been exceeded and an additional coupler is needed |  | Example: | 10260
Other guidelines when putting together a remote I/O block
An AKT2G-EM-000-000 End Module provides protection for side plane logic contacts on last slice in the block
24 Volt power module – AKT2G-PSF-024-000 will provides a gateway to bring in additional 24 VDC power to the slices. The 24 VDC is applied to the slices mounted to the right of the slice
For high speed inputs, the AKT-DNH-00x-000 Digital Input Modules offer very fast response but have less signal filtering (of high frequency spikes).
Define the Applications Input I/O Slice Configuration Here